## perimeter
Perimeter of the blocks of the A2 map- 10096.39
number of connections will be- 403.8544 | 404

## water
Count of connections | Persons per connection | Persons | Secific water demand | Average water demand | Seasonal ratio | Peak water demand | Loss coefficient | Designing peak water demand
piece | person/binding in | head | l/person/day | m3/day | - | m3/day | - | m3/day
404 | 2.6 | 1050.4 | 140 | 147.056 | 1.2 | 176.4672 | 1.1 | 194.1139
PUBLIC INSTITUTIONS WATER DEMAND
Profession of people | Number of people | specific water demand | average water demand | seasonal ratio | peak water demand | loss coefficient | designing peak water demand
|  | l/person/day | m3/day | - | m3/day | - | m3/day
worker | 30 | 160 | 4.8 | 1.5 | 7.2 | 1.1 | 7.92
student | 500 | 160 | 80 | 1.5 | 120 | 1.1 | 132
SUM | [6 empty] | 139.92
THE INDUSTRIAL WATER DEMAND
Technological water demand | loss coefficient | designing peak water demand
m3/day | - | m3/day
1000 | 1.1 | 1100
Number of people | specific water demand | average water demand | seasonal ratio | peak water demand | loss coefficient | designing peak water demand
| l/person/day | m3/day | - | m3/day | - | m3/day
100 | 100 | 10 | 1.2 | 12 | 1.1 | 13.2 |  | total consumption will be | 1447.2339

## cons.nodes
Branches | Length | Q branches | Q node 1 | Q node 2 | Node | Branch (m3/day) | [9 empty] | Node |  |  | Q dweller | Q public ins. | Q ind. soc. | Q people | Q ind. tech. | Q fire
| m | m3/day | m3/day | m3/day | m3/day | 1-2 | 2-3 | 3-4 | 4-5 | 5-6 | 6-7 | 7-8 | 8-9 | 9-10 | 10 2 | m3/day |  | Node | m3/day | m3/day | m3/day | m3/day | m3/day | l/min
1 2 | 76 | 28.478 | 14.239 | 14.239 | 1 | Branch (m3/day) 1-2: 14.239 |  | 14.239 |  | 1 | 14.239 |  |  | 14.239
2 3 | 56 | 20.9838 | 10.4919 | 10.4919 | 2 | Branch (m3/day) 1-2: 14.239; Branch (m3/day) 2-3: 10.4919 | 8.8057 | 33.5366 |  | 2 | 33.5366 |  |  | 33.5366
3 4 | 56 | 20.9838 | 10.4919 | 10.4919 | 3 | Branch (m3/day) 2-3: 10.4919; Branch (m3/day) 3-4: 10.4919 |  | 20.9838 |  | 3 | 20.9838 |  |  | 20.9838
4 5 | 47 | 17.6114 | 8.8057 | 8.8057 | 4 | Branch (m3/day) 3-4: 10.4919; Branch (m3/day) 4-5: 8.8057 |  | 19.2976 |  | 4 | 19.2976 |  |  | 19.2976
5 6 | 45 | 16.862 | 8.431 | 8.431 | 5 | Branch (m3/day) 4-5: 8.8057; Branch (m3/day) 5-6: 8.431 |  | 17.2367 |  | 5 | 17.2367 |  |  | 17.2367
6 7 | 48 | 17.9861 | 8.9931 | 8.9931 | 6 | Branch (m3/day) 5-6: 8.431; Branch (m3/day) 6-7: 8.9931 |  | 17.424 | school | 6 | 17.424 | 139.9 |  | 157.324
7 8 | 49 | 18.3608 | 9.1804 | 9.1804 | 7 | Branch (m3/day) 6-7: 8.9931; Branch (m3/day) 7-8: 9.1804 |  | 18.1735 |  | 7 | 18.1735 |  |  | 18.1735
8 9 | 40 | 14.9884 | 7.4942 | 7.4942 | 8 | Branch (m3/day) 7-8: 9.1804; Branch (m3/day) 8-9: 7.4942 |  | 16.6746 | industry | 8 | 16.6746 |  | 13.2 | 29.8746 | 1100
9 10 | 54 | 20.2344 | 10.1172 | 10.1172 | 9 | Branch (m3/day) 8-9: 7.4942; Branch (m3/day) 9-10: 10.1172 |  | 17.6114 |  | 9 | 17.6114 |  |  | 17.6114
10 2 | 47 | 17.6114 | 8.8057 | 8.8057 | 10 | Branch (m3/day) 9-10: 10.1172 | 8.8057 | 18.9229 | fire | 10 | 18.9229 |  |  | 18.9229 |  | 1200
SUM | 518 | 194.1 | [15 empty] | SUM | 194.1 | 139.9 | 13.2 | 347.2 | 1100 | 1200
1447.2

## max-min aver
1% |  | Q people | Q ind tech | Q fire | Q people | Q ind. tech | Q fire | Q node
| Node | m3/day | m3/day | l/min | l/s
| 1 | 14.239 |  |  | 0.039553 |  | - | 0.039553
| 2 | 33.5366 |  |  | 0.093157 |  | - | 0.093157
| 3 | 20.9838 |  |  | 0.058288 |  | - | 0.058288
| 4 | 19.2976 |  |  | 0.053604 |  | - | 0.053604
| 5 | 17.2367 |  |  | 0.04788 |  | - | 0.04788
| 6 | 157.324 |  |  | 0.43701 |  | - | 0.43701
| 7 | 18.1735 |  |  | 0.050482 |  | - | 0.050482
| 8 | 29.8746 | 1100 |  | 0.082985 | 12.7315 | - | 12.8145
| 9 | 17.6114 |  |  | 0.048921 |  | - | 0.048921
| 10 | 18.9229 |  | 1200 | 0.052564 |  | - | 0.052564
| Q cons | 347.2 | 1100 | 1200 | 0.96444 | 12.7315 | - | 13.6959
maximum consumption (8 %)
|  | Q people | Q ind tech | Q fire | Q people | Q ind. tech | Q fire | Q node
| Node | m3/day | m3/day | l/min | l/s
| 1 | 14.239 |  |  | 0.31642 |  | - | 0.31642
| 2 | 33.5366 |  |  | 0.74526 |  | - | 0.74526
| 3 | 20.9838 |  |  | 0.46631 |  | - | 0.46631
| 4 | 19.2976 |  |  | 0.42884 |  | - | 0.42884
| 5 | 17.2367 |  |  | 0.38304 |  | - | 0.38304
| 6 | 157.324 |  |  | 3.4961 |  | - | 3.4961
| 7 | 18.1735 |  |  | 0.40385 |  | - | 0.40385
| 8 | 29.8746 | 1100 |  | 0.66388 | 12.7315 | - | 13.3954
| 9 | 17.6114 |  |  | 0.39136 |  | - | 0.39136
| 10 | 18.9229 |  | 900 | 0.42051 |  | - | 0.42051
| Q cons | 347.2 | 1100 | 900 | 7.7156 | 12.7315 | - | 20.447
average consumption (4.17 %) + fire
|  | Q people | Q ind tech | Q fire | Q people | Q ind. tech | Q fire | Q node
| Node | m3/day | m3/day | l/min | l/s
| 1 | 14.239 |  |  | 0.1648 |  |  | 0.1648
| 2 | 33.5366 |  |  | 0.38815 |  |  | 0.38815
| 3 | 20.9838 |  |  | 0.24287 |  |  | 0.24287
| 4 | 19.2976 |  |  | 0.22335 |  |  | 0.22335
| 5 | 17.2367 |  |  | 0.1995 |  |  | 0.1995
| 6 | 157.324 |  |  | 1.8209 |  |  | 1.8209
| 7 | 18.1735 |  |  | 0.21034 |  |  | 0.21034
| 8 | 29.8746 | 1100 |  | 0.34577 | 12.7315 |  | 13.0773
| 9 | 17.6114 |  |  | 0.20384 |  |  | 0.20384
| 10 | 18.9229 |  | 900 | 0.21901 |  | 15 | 15.219
| Q cons | 347.2 | 1100 | 900 | 4.0185 | 12.7315 | 15 | 31.75

## initial
maximum consumption
| Branch | Qin (l/s) | Node | Qnode (l/s) | Branches | Qbranch (l/s)
|  | 20.447 | 1 | 0.31642 | 1-2 | 20.1306
| 1-2 | 20.1306 | 2 | 0.74526 | 2-3 | 9.6927
| 2-3 | 9.6927 | 3 | 0.46631 | 3-4 | 9.2264
| 3-4 | 9.2264 | 4 | 0.42884 | 4-5 | 8.7975
| 4-5 | 8.7975 | 5 | 0.38304 | 5-6 | 8.4145
| 5-6 | 8.4145 | 6 | 3.4961 | 6-7 | 4.9184
| 6-7 | 4.9184 | 7 | 0.40385 | 7-8 | 4.5146
| 7-8 | 4.5146 | 8 | 13.3954 | 8-9 | -8.8808
| 8-9 | -8.8808 | 9 | 0.39136 | 9-10 | -9.2722
| 9-10 | -9.2722 | 10 | 0.42051 | 10-11 | -9.6927
| 10-2 | -9.6927
average consumption | [6 empty] | min cons
Branch | Qin (l/s) | Node | Qnode (l/s) | Branches | Qbranch (l/s) |  | Branch | Qin (l/s) | Node | Qnode (l/s) | Branches | Qbranch (l/s)
| 31.75 | 1 | 0.1648 | 1-2 | 31.5852 |  |  | 13.6959 | 1 | 0.039553 | 1 2 | 13.6564
1-2 | 31.5852 | 2 | 0.38815 | 2-3 | 15.5985 |  | 1-2 | 13.6564 | 2 | 0.093157 | 2 3 | 6.7816
2-3 | 15.5985 | 3 | 0.24287 | 3-4 | 15.3557 |  | 2-3 | 6.7816 | 3 | 0.058288 | 3 4 | 6.7233
3-4 | 15.3557 | 4 | 0.22335 | 4-5 | 15.1323 |  | 3-4 | 6.7233 | 4 | 0.053604 | 4 5 | 6.6697
4-5 | 15.1323 | 5 | 0.1995 | 5-6 | 14.9328 |  | 4-5 | 6.6697 | 5 | 0.04788 | 5 6 | 6.6218
5-6 | 14.9328 | 6 | 1.8209 | 6-7 | 13.1119 |  | 5-6 | 6.6218 | 6 | 0.43701 | 6 7 | 6.1848
6-7 | 13.1119 | 7 | 0.21034 | 7-8 | 12.9016 |  | 6-7 | 6.1848 | 7 | 0.050482 | 7 8 | 6.1343
7-8 | 12.9016 | 8 | 13.0773 | 8-9 | -0.17567 |  | 7-8 | 6.1343 | 8 | 12.8145 | 8 9 | -6.6801
8-9 | -0.17567 | 9 | 0.20384 | 9-10 | -0.37951 |  | 8-9 | -6.6801 | 9 | 0.048921 | 9 10 | -6.729
9-10 | -0.37951 | 10 | 15.219 | 10-11 | -15.5985 |  | 9-10 | -6.729 | 10 | 0.052564 | 10 2 | -6.7816
$10-2 | -15.5985 | [5 empty] | 10 2 | -6.7816

## diameter
Branch | Qbranch (l/s) | Qbranch (m3/s) | Calculated diameter (m) | Diameter (mm)
1-2 | 20.1306 | 0.020131 | 0.1601 | 200
2-3 | 9.6927 | 0.0096927 | 0.11109 | 175
3-4 | 9.2264 | 0.0092264 | 0.10839 | 175
4-5 | 8.7975 | 0.0087975 | 0.10584 | 175
5-6 | 8.4145 | 0.0084145 | 0.10351 | 175
6-7 | 4.9184 | 0.0049184 | 0.079135 | 175
7-8 | 4.5146 | 0.0045146 | 0.075816 | 175
8-9 | -8.8808 | -0.0088808 | 0.10634 | 175
9-10 | -9.2722 | -0.0092722 | 0.10865 | 175
10-2 | -9.6927 | -0.0096927 | 0.11109 | 175

## cross
MAXIMUM CONSUMPTION | [5 empty] | 1. iteration | [5 empty] | 2. iteration
Branch | Lenght (m) | Diameter (mm) | main-ring | Sign | C [s2/m5] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ | Q[m3/s] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ | [7 empty] | ΔQ
1-2 | 76 | 200 | branch | 1 | 647.588 | 0.020131 | 26.0727 | 0.26243 |  |  |  | 0.020131 | 0.020131
2-3 | 56 | 175 |  | 1 | 930.3213 | 0.0096927 | 18.0346 | 0.087402 | 18.0346 | 0.087402 |  | 0.0087537 | 0.0087537 | 16.2875 | 0.071288 | 16.2875 | 0.071288
3-4 | 56 | 175 |  | 1 | 930.3213 | 0.0092264 | 17.167 | 0.079194 | 35.2016 | 0.1666 |  | 0.0082874 | 0.0082874 | 15.4199 | 0.063895 | 31.7074 | 0.13518
4-5 | 47 | 175 |  | 1 | 780.8054 | 0.0087975 | 13.7383 | 0.060432 | 48.9399 | 0.22703 |  | 0.0078586 | 0.0078586 | 12.272 | 0.04822 | 43.9794 | 0.1834
5-6 | 45 | 175 |  | 1 | 747.5796 | 0.0084145 | 12.581 | 0.052931 | 61.5209 | 0.27996 |  | 0.0074755 | 0.0074755 | 11.1771 | 0.041777 | 55.1565 | 0.22518
6-7 | 48 | 175 |  | 1 | 797.4182 | 0.0049184 | 7.8441 | 0.01929 | 69.365 | 0.29925 |  | 0.0039794 | 0.0039794 | 6.3465 | 0.012628 | 61.503 | 0.23781
7-8 | 49 | 175 |  | 1 | 814.0311 | 0.0045146 | 7.35 | 0.016591 | 76.715 | 0.31584 |  | 0.0035756 | 0.0035756 | 5.8213 | 0.010407 | 67.3243 | 0.24822
8-9 | 40 | 175 |  | 1 | 664.5152 | -0.0088808 | 11.8029 | -0.052409 | 88.5178 | 0.26343 |  | -0.0098198 | -0.0098198 | 13.0508 | -0.064078 | 80.3751 | 0.18414
9-10 | 54 | 175 |  | 1 | 897.0955 | -0.0092722 | 16.636 | -0.077126 | 105.1539 | 0.18631 |  | -0.010211 | -0.010211 | 18.3208 | -0.093538 | 98.6958 | 0.0906
10 2 | 47 | 175 |  | 1 | 780.8054 | -0.0096927 | 15.1362 | -0.073355 | 120.2901 | 0.11295 | -0.00093898 | -0.010632 | -0.010632 | 16.6025 | -0.088256 | 115.2983 | 0.0023436 | 2.0326e-05
[10 empty] | failure | [6 empty] | failure
MINIMUM CONSUMPTION | [5 empty] | 1. iteration | [5 empty] | 2. iteration
Branch | Lenght (m) | Diameter (mm) | main-ring | Sign | C [s2/m5] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ | Q[m3/s] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ
1-2 | 76 | 200 | branch | 1 | 647.588 | 0.022233 | 28.795 | 0.32009 |  |  |  | 0.022233 | 0.022233
2-3 | 56 | 175 |  | 1 | 930.3213 | 0.011019 | 20.5021 | 0.11295 | 20.5021 | 0.11295 |  | 0.0091728 | 0.0091728 | 17.0673 | 0.078278 | 17.0673 | 0.078278
3-4 | 56 | 175 |  | 1 | 930.3213 | 0.010892 | 20.2653 | 0.11036 | 40.7673 | 0.22331 |  | 0.0090455 | 0.0090455 | 16.8305 | 0.076121 | 33.8978 | 0.1544
4-5 | 47 | 175 |  | 1 | 780.8054 | 0.010777 | 16.8294 | 0.090685 | 57.5968 | 0.314 |  | 0.008931 | 0.008931 | 13.9467 | 0.062279 | 47.8446 | 0.21668
5-6 | 45 | 175 |  | 1 | 747.5796 | 0.010645 | 15.9165 | 0.084718 | 73.5132 | 0.39872 |  | 0.0087993 | 0.0087993 | 13.1564 | 0.057884 | 61.001 | 0.27456
6-7 | 48 | 175 | one-loop | 1 | 797.4182 | 0.010066 | 16.0532 | 0.080793 | 89.5664 | 0.47951 |  | 0.0082197 | 0.0082197 | 13.1091 | 0.053877 | 74.1101 | 0.32844
7-8 | 49 | 175 |  | 1 | 814.0311 | 0.0099711 | 16.2335 | 0.080933 | 105.7999 | 0.56044 |  | 0.0081251 | 0.0081251 | 13.2281 | 0.05374 | 87.3382 | 0.38218
8-9 | 40 | 175 |  | 1 | 664.5152 | -0.010653 | 14.158 | -0.075412 | 119.9579 | 0.48503 |  | -0.012499 | -0.012499 | 16.6114 | -0.10381 | 103.9496 | 0.27837
9-10 | 54 | 175 |  | 1 | 897.0955 | -0.010768 | 19.3203 | -0.10402 | 139.2782 | 0.38101 |  | -0.012614 | -0.012614 | 22.6323 | -0.14274 | 126.5819 | 0.13562
10-11 | 47 | 175 |  | 1 | 780.8054 | -0.010886 | 16.999 | -0.092522 | 156.2772 | 0.28849 | -0.001846 | -0.012732 | -0.012732 | 19.8817 | -0.12656 | 146.4637 | 0.0090579 | -6.1844e-05
[10 empty] | failure | [6 empty] | failure
AVERAGE CONSUMPTION | [5 empty] | 1. iteration | [5 empty] | 2. iteration | [6 empty] | 3. iteration
Branch | Lenght (m) | Diameter (mm) | main-ring | Sign | C [s2/m5] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ | Q[m3/s] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ | Q[m3/s] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ
1-2 | 90 | 200 | branch | 1 | 766.8805 | 0.043129 | 66.1501 | 1.4265 |  |  |  | 0.043129 | 0.043129 | [5 empty] | 0.043129 | 0.043129
2-3 | 205 | 150 |  | 1 | 7360.9309 | 0.021159 | 311.4946 | 3.2954 | 311.4946 | 3.2954 |  | 0.014829 | 0.014829 | 218.3159 | 1.6187 | 218.3159 | 1.6187 |  | 0.014339 | 0.014339 | 211.09 | 1.5134 | 211.09 | 1.5134
3-4 | 115 | 150 |  | 1 | 4129.3027 | 0.020628 | 170.361 | 1.7571 | 481.8556 | 5.0525 |  | 0.014299 | 0.014299 | 118.09 | 0.84429 | 336.406 | 2.463 |  | 0.013808 | 0.013808 | 114.0365 | 0.78732 | 325.1264 | 2.3007
4-5 | 173 | 150 |  | 1 | 6211.9075 | 0.020151 | 250.3522 | 2.5224 | 732.2079 | 7.575 |  | 0.013822 | 0.013822 | 171.7185 | 1.1867 | 508.1245 | 3.6498 |  | 0.013331 | 0.013331 | 165.6205 | 1.1039 | 490.747 | 3.4046
5-6 | 158 | 150 |  | 1 | 5673.3028 | 0.019602 | 222.421 | 2.18 | 954.6289 | 9.755 |  | 0.013273 | 0.013273 | 150.6052 | 0.9995 | 658.7297 | 4.6493 |  | 0.012782 | 0.012782 | 145.0359 | 0.92695 | 635.7829 | 4.3316
6-7 | 110 | 150 | one-loop | 1 | 3949.7678 | 0.017187 | 135.7727 | 1.1668 | 1090.4016 | 10.9217 |  | 0.010858 | 0.010858 | 85.7744 | 0.46568 | 744.5041 | 5.1149 |  | 0.010367 | 0.010367 | 81.8971 | 0.42453 | 717.68 | 4.7561
7-8 | 128 | 150 |  | 1 | 4596.0934 | 0.016793 | 154.3643 | 1.2961 | 1244.7659 | 12.2179 |  | 0.010464 | 0.010464 | 96.1844 | 0.50322 | 840.6885 | 5.6182 |  | 0.0099729 | 0.0099729 | 91.6726 | 0.45712 | 809.3526 | 5.2132
8-9 | 135 | 150 |  | 1 | 4847.4423 | -0.0046339 | 44.9253 | -0.10409 | 1289.6912 | 12.1138 |  | -0.010963 | -0.010963 | 106.2868 | -0.58262 | 946.9754 | 5.0355 |  | -0.011454 | -0.011454 | 111.0454 | -0.63596 | 920.398 | 4.5773
9-10 | 155 | 150 |  | 1 | 5565.5819 | -0.0051145 | 56.9307 | -0.14559 | 1346.6219 | 11.9682 |  | -0.011444 | -0.011444 | 127.3829 | -0.72887 | 1074.3583 | 4.3067 |  | -0.011935 | -0.011935 | 132.8464 | -0.79274 | 1053.2444 | 3.7845
10-11 | 140 | 150 |  | 1 | 5026.9772 | -0.020603 | 207.1461 | -2.134 | 1553.768 | 9.8342 | -0.0063293 | -0.026933 | -0.026933 | 270.7803 | -3.6464 | 1345.1386 | 0.66024 | -0.00049083 | -0.027424 | -0.027424 | 275.7151 | -3.7805 | 1328.9595 | 0.0039706 | -2.9878e-06
[10 empty] | failure | [6 empty] | failure | [6 empty] | failure

## pressure flow loss
MAXIMUM CONSUMPTION
Branches | Lenght (m) | Diameter (mm) | Q (m3/s) | Q (l/s) | water velocity (m/s) | local loss (hL) C*Q*abs(Q) (m) | specific pressure flow loss ‰
1-2 | 76 | 200 | 0.020131 | 20.1306 | 0.64078 | 0.26243 | 3.453
2-3 | 56 | 175 | 0.0087537 | 8.7537 | 0.36394 | 0.071288 | 1.273
3-4 | 56 | 175 | 0.0082874 | 8.2874 | 0.34455 | 0.063895 | 1.141
4-5 | 47 | 175 | 0.0078586 | 7.8586 | 0.32672 | 0.04822 | 1.026
5-6 | 45 | 175 | 0.0074755 | 7.4755 | 0.3108 | 0.041777 | 0.92838
6-7 | 48 | 175 | 0.0039794 | 3.9794 | 0.16545 | 0.012628 | 0.26308
7-8 | 49 | 175 | 0.0035756 | 3.5756 | 0.14866 | 0.010407 | 0.21239
8-9 | 40 | 175 | -0.0098198 | -9.8198 | -0.40826 | -0.064078 | -1.602
9-10 | 54 | 175 | -0.010211 | -10.2111 | -0.42453 | -0.093538 | -1.7322
10 2 | 47 | 175 | -0.010632 | -10.6317 | -0.44201 | -0.088256 | -1.8778
MINIMUM CONSUMPTION
Branches | Lenght (m) | Diameter (mm) | Q (m3/s) | Q (l/s) | water velocity (m/s) | local loss (hL) C*Q*abs(Q) (m) | specific pressure flow loss ‰
1-2 | 76 | 200 | 0.022233 | 22.2325 | 0.70768 | 0.32009 | 4.2118
2-3 | 56 | 175 | 0.0091728 | 9.1728 | 0.38136 | 0.078278 | 1.3978
3-4 | 56 | 175 | 0.0090455 | 9.0455 | 0.37607 | 0.076121 | 1.3593
4-5 | 47 | 175 | 0.008931 | 8.931 | 0.37131 | 0.062279 | 1.3251
5-6 | 45 | 175 | 0.0087993 | 8.7993 | 0.36583 | 0.057884 | 1.2863
6-7 | 48 | 175 | 0.0082197 | 8.2197 | 0.34174 | 0.053877 | 1.1224
7-8 | 49 | 175 | 0.0081251 | 8.1251 | 0.3378 | 0.05374 | 1.0967
8-9 | 40 | 175 | -0.012499 | -12.4989 | -0.51964 | -0.10381 | -2.5953
9-10 | 54 | 175 | -0.012614 | -12.6142 | -0.52444 | -0.14274 | -2.6434
10 2 | 47 | 175 | -0.012732 | -12.7316 | -0.52932 | -0.12656 | -2.6928
AVERAGE CONSUMPTION
Branches | Lenght (m) | Diameter (mm) | Q (m3/s) | Q (l/s) | water velocity (m/s) | local loss (hL) C*Q*abs(Q) (m) | specific pressure flow loss ‰
1-2 | 76 | 200 | 0.043129 | 43.1294 | 1.3729 | 1.4265 | 18.7698
2-3 | 56 | 175 | 0.014339 | 14.3385 | 0.59613 | 1.5134 | 27.0243
3-4 | 56 | 175 | 0.013808 | 13.8082 | 0.57408 | 0.78732 | 14.0593
4-5 | 47 | 175 | 0.013331 | 13.3309 | 0.55423 | 1.1039 | 23.488
5-6 | 45 | 175 | 0.012782 | 12.7823 | 0.53143 | 0.92695 | 20.5988
6-7 | 48 | 175 | 0.010367 | 10.3673 | 0.43102 | 0.42453 | 8.8443
7-8 | 49 | 175 | 0.0099729 | 9.9729 | 0.41462 | 0.45712 | 9.329
8-9 | 40 | 175 | -0.011454 | -11.454 | -0.4762 | -0.63596 | -15.899
9-10 | 54 | 175 | -0.011935 | -11.9346 | -0.49618 | -0.79274 | -14.6803
10 2 | 47 | 175 | -0.027424 | -27.4235 | -1.1401 | -3.7805 | -80.4371

## node pressure
MAXIMUM CONSUMPTION
Node A |  | Branch |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above see) |  | (hL) C*Q*abs(Q) |  | H (m above see) | (m above see) | h (m) | H demand (m)
1 | 68 | 1-2 | 0.95385 | 2 | 67.0461 | 35.5 | 31.5461 | 25 | OK
2 | 67.0461 | 2-3 | 1.9575 | 3 | 65.0886 | 36 | 29.0886 | 25 | OK
3 | 65.0886 | 3-4 | 0.96527 | 4 | 64.1233 | 36 | 28.1233 | 25 | OK
4 | 64.1233 | 4-5 | 1.2832 | 5 | 62.8401 | 36.5 | 26.3401 | 25 | OK
5 | 62.8401 | 5-6 | 1.0065 | 6 | 61.8336 | 36 | 25.8336 | 25 | OK
6 | 61.8336 | 6-7 | 0.29778 | 7 | 61.5358 | 36 | 25.5358 | 25 | OK
7 | 61.5358 | 7-8 | 0.28869 | 8 | 61.2471 | 36 | 25.2471 | 25 | OK
8 | 61.2471 | 8-9 | -1.0154 | 9 | 62.2626 | 35.5 | 26.7626 | 25 | OK
9 | 62.2626 | 9-10 | -1.3193 | 10 | 63.5819 | 36 | 27.5819 | 25 | OK
10 | 63.5819 | 10-11 | -1.3414 | 2 | 64.9232 | 36.5 | 28.4232 | 25 | OK
67.0461
MINIMUM CONSUMPTION
Node A |  | Branch |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above see) |  | (hL) C*Q*abs(Q) |  | H (m above see) | (m above see) | h (m) | H demand (m)
1 | 68 | 1-2 | 0.32009 | 2 | 67.6799 | 35.5 | 32.1799 | 25 | OK
2 | 67.6799 | 2-3 | 0.078278 | 3 | 67.6016 | 36 | 31.6016 | 25 | OK
3 | 67.6016 | 3-4 | 0.076121 | 4 | 67.5255 | 36 | 31.5255 | 25 | OK
4 | 67.5255 | 4-5 | 0.062279 | 5 | 67.4632 | 36.5 | 30.9632 | 25 | OK
5 | 67.4632 | 5-6 | 0.057884 | 6 | 67.4053 | 36 | 31.4053 | 25 | OK
6 | 67.4053 | 6-7 | 0.053877 | 7 | 67.3515 | 36 | 31.3515 | 25 | OK
7 | 67.3515 | 7-8 | 0.05374 | 8 | 67.2977 | 36 | 31.2977 | 25 | OK
8 | 67.2977 | 8-9 | -0.10381 | 9 | 67.4015 | 35.5 | 31.9015 | 25 | OK
9 | 67.4015 | 9-10 | -0.14274 | 10 | 67.5443 | 36 | 31.5443 | 25 | OK
10 | 67.5443 | 10-11 | -0.12656 | 2 | 67.6708 | 36.5 | 31.1708 | 25 | OK
0.0090579
AVERAGE CONSUMPTION
Node A |  | Branch |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above see) |  | (hL) C*Q*abs(Q) |  | H (m above see) | (m above see) | h (m) | H demand (m)
1 | 68 | 1-2 | 1.4265 | 2 | 66.5735 | 35.5 | 31.0735 | 25 | OK
2 | 66.5735 | 2-3 | 1.5134 | 3 | 65.0601 | 36 | 29.0601 | 25 | OK
3 | 65.0601 | 3-4 | 0.78732 | 4 | 64.2728 | 36 | 28.2728 | 25 | OK
4 | 64.2728 | 4-5 | 1.1039 | 5 | 63.1689 | 36.5 | 26.6689 | 25 | OK
5 | 63.1689 | 5-6 | 0.92695 | 6 | 62.2419 | 36 | 26.2419 | 25 | OK
6 | 62.2419 | 6-7 | 0.42453 | 7 | 61.8174 | 36 | 25.8174 | 25 | OK
7 | 61.8174 | 7-8 | 0.45712 | 8 | 61.3603 | 36 | 25.3603 | 25 | OK
8 | 61.3603 | 8-9 | -0.63596 | 9 | 61.9962 | 35.5 | 26.4962 | 25 | OK
9 | 61.9962 | 9-10 | -0.79274 | 10 | 62.789 | 36 | 26.789 | 25 | OK
10 | 62.789 | 10-11 | -3.7805 | 2 | 66.5695 | 36.5 | 30.0695 | 25 | OK
0.0039706

## pressure profile
MAXIMUM CONSUMPTION
Node A |  | Branch |  |  |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above sea) |  | Length (m) | ΣLength (m) | (hL) C*Q*abs(Q) |  | H (m above sea) | (m above sea) | h (m) | H demand (m)
1 | 68 | 1-2 | 76 | 76 | 0.26243 | 2 | 67.7376 | 35.5 | 32.2376 | 25 | OK
2 | 67.7376 | 2-3 | 56 | 132 | 0.071288 | 3 | 67.6663 | 36 | 31.6663 | 25 | OK
3 | 67.6663 | 3-4 | 56 | 188 | 0.063895 | 4 | 67.6024 | 36 | 31.6024 | 25 | OK
4 | 67.6024 | 4-5 | 47 | 235 | 0.04822 | 5 | 67.5542 | 36.5 | 31.0542 | 25 | OK
5 | 67.5542 | 5-6 | 45 | 280 | 0.041777 | 6 | 67.5124 | 36 | 31.5124 | 25 | OK
6 | 67.5124 | 6-7 | 48 | 328 | 0.012628 | 7 | 67.4998 | 36 | 31.4998 | 25 | OK
7 | 67.4998 | 7-8 | 49 | 377 | 0.010407 | 8 | 67.4894 | 36 | 31.4894 | 25 | OK
8 | 67.4894 | 8-9 | 40 | 417 | -0.064078 | 9 | 67.5534 | 35.5 | 32.0534 | 25 | OK
9 | 67.5534 | 9-10 | 54 | 471 | -0.093538 | 10 | 67.647 | 36 | 31.647 | 25 | OK
10 | 67.647 | 10-11 | 47 | 518 | -0.088256 | 11 | 67.7352 | 36.5 | 31.2352 | 25 | OK
0.0023436
MINIMUM CONSUMPTION
Node A |  | Branch |  |  |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above sea) |  | Length (m) | ΣLength (m) | (hL) C*Q*abs(Q) |  | H (m above sea) | (m above sea) | h (m) | H demand (m)
1 | 68 | 1-2 | 76 | 76 | 0.32009 | 2 | 67.6799 | 35.5 | 32.1799 | 25 | OK
2 | 67.6799 | 2-3 | 56 | 132 | 0.078278 | 3 | 67.6016 | 36 | 31.6016 | 25 | OK
3 | 67.6016 | 3-4 | 56 | 188 | 0.076121 | 4 | 67.5255 | 36 | 31.5255 | 25 | OK
4 | 67.5255 | 4-5 | 47 | 235 | 0.062279 | 5 | 67.4632 | 36.5 | 30.9632 | 25 | OK
5 | 67.4632 | 5-6 | 45 | 280 | 0.057884 | 6 | 67.4053 | 36 | 31.4053 | 25 | OK
6 | 67.4053 | 6-7 | 48 | 328 | 0.053877 | 7 | 67.3515 | 36 | 31.3515 | 25 | OK
7 | 67.3515 | 7-8 | 49 | 377 | 0.05374 | 8 | 67.2977 | 36 | 31.2977 | 25 | OK
8 | 67.2977 | 8-9 | 40 | 417 | -0.10381 | 9 | 67.4015 | 35.5 | 31.9015 | 25 | OK
9 | 67.4015 | 9-10 | 54 | 471 | -0.14274 | 10 | 67.5443 | 36 | 31.5443 | 25 | OK
10 | 67.5443 | 10-11 | 47 | 518 | -0.12656 | 2 | 67.6708 | 36.5 | 31.1708 | 25 | OK
0.0090579
AVERAGE CONSUMPTION
Node A |  | Branch |  |  |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above sea) |  | Length (m) | ΣLength (m) | (hL) C*Q*abs(Q) |  | H (m above sea) | (m above sea) | h (m) | H demand (m)
1 | 68 | 1-2 | 76 | 76 | 1.4265 | 2 | 66.5735 | 35.5 | 31.0735 | 25 | OK
2 | 66.5735 | 2-3 | 56 | 132 | 1.5134 | 3 | 65.0601 | 36 | 29.0601 | 25 | OK
3 | 65.0601 | 3-4 | 56 | 188 | 0.78732 | 4 | 64.2728 | 36 | 28.2728 | 25 | OK
4 | 64.2728 | 4-5 | 47 | 235 | 1.1039 | 5 | 63.1689 | 36.5 | 26.6689 | 25 | OK
5 | 63.1689 | 5-6 | 45 | 280 | 0.92695 | 6 | 62.2419 | 36 | 26.2419 | 25 | OK
6 | 62.2419 | 6-7 | 48 | 328 | 0.42453 | 7 | 61.8174 | 36 | 25.8174 | 25 | OK
7 | 61.8174 | 7-8 | 49 | 377 | 0.45712 | 8 | 61.3603 | 36 | 25.3603 | 25 | OK
8 | 61.3603 | 8-9 | 40 | 417 | -0.63596 | 9 | 61.9962 | 35.5 | 26.4962 | 25 | OK
9 | 61.9962 | 9-10 | 54 | 471 | -0.79274 | 10 | 62.789 | 36 | 26.789 | 25 | OK
10 | 62.789 | 10-11 | 47 | 518 | -3.7805 | 11 | 66.5695 | 36.5 | 30.0695 | 25 | OK
0.0039706