## wastewaterdemand
|  | Point number | Catchment | Catchment areas | Waste water load due to : |  |  |  | Total design load
[5 empty] | Inhabitants | Public institution | Communal demand | Technological demand
|  |  |  | [m2] | [m3/h] | [m3/h] | [m3/h] | [m3/h] | [m3/h]
|  | 1 | S1 + S2 + S3 + S4+S5+S6 | 15643.8 | 194.1139 | 5.5968 | 0.528 | 44 | 244.2387
|  | 1 | S3+S4 | 4936.7 | 61.2564 |  | 0.528 | 44 | 105.7844
|  | 2 | S2+S5+S6 | 6819.6 | 84.6201 |  |  |  | 84.6201
|  | 3 | S4 | 3250.3 | 40.3309 | 5.5968 |  |  | 45.9277
|  | 4 | S5 | 2273.7 | 28.2129 |  | 0.528 | 44 | 72.7409
|  | 5 | S6 | 3117.7 | 38.6855 |  |  |  | 38.6855
|  | Total. |  | 15643.8
Derivation of waste water | maximum water consumption (m3/day) | Waste water fraction / sewage ratio | Maximum waste water quantity (m3/day) | hourly-peak ratio | hourly maximum waste water quantity (m3/hour)
dweller | 194.1139 | 0.8 | 155.2911 | 0.05 | 7.7646
public institution | 139.92 | 0.8 | 111.936 | 0.05 | 5.5968
technological water | 1100 | 0.8 | 880 | 0.05 | 44
social water | 13.2 | 0.8 | 10.56 | 0.05 | 0.528
Pipe number | Length of the pipes | Depth of the inlet point of the pipe | Depth of the outlet point of the pipe | Slope
| [m] | [m] | [m] | [‰]
0 | 181.6818 | 4.8183 | 5 | 1
1 | 89.2556 | 4.7291 | 4.8183 | 1
2 | 45.4376 | 4.6836 | 4.7291 | 1
3 | 103.5179 | 4.5801 | 4.6836 | 1
4 | 111.0871 | 4.469 | 4.5801 | 1
5
Pipe number | Slope | Roughness of the pipe | Diameter of the pipes d | vtot | Qtot | Qdesign | Qdesign/Qtot
| [‰] | [mm] | [m] | [m/s] | [L/s] | [L/s]
0 | 1 | 0.5 | 0.5 | 0.68812 | 135.1114 | 67.8441 | 0.50213
1 | 1 | 0.5 | 0.5 | 0.68812 | 135.1114 | 29.3845 | 0.21748
2 | 1 | 0.5 | 0.5 | 0.68812 | 135.1114 | 23.5056 | 0.17397
3 | 1 | 0.5 | 0.5 | 0.68812 | 135.1114 | 12.7577 | 0.094424
4 | 1 | 0.5 | 0.5 | 0.68812 | 135.1114 | 20.2058 | 0.14955
5 | 1 | 0.5 | 0.5 | 0.68812 | 135.1114 | 10.746 | 0.079534
Pipe number | Qdesign/Qtot | vdesign/vtot | h/d | Diameter of the pipes d | h | vtot | vreal
| [%] | [%] | [%] | [m] | [m] | [m/s] | [m/s]
0 | 50.2135 | 89 | 55 | 0.5 | 0.275 | 0.68812 | 0.61242
1 | 21.7484 | 69 | 38 | 0.5 | 0.19 | 0.68812 | 0.4748
2 | 17.3972 | 78 | 42 | 0.5 | 0.21 | 0.68812 | 0.53673
3 | 9.4424 | 65 | 31 | 0.5 | 0.155 | 0.68812 | 0.44728
4 | 14.9549 | 71 | 39 | 0.5 | 0.195 | 0.68812 | 0.48856
5 | 7.9534 | 58 | 29 | 0.5 | 1.7241 | 0.68812 | 0.39911

## waterdemand
Count of connections | Persons per connection | Persons | Specific water demand | Average water demand | Seasonal ratio | Peak water demand | Loss coefficient | Designing peak water demand
piece | person/binding in | head | l/person/day | m3/day | - | m3/day | - | m3/day
404 | 2.6 | 1050.4 | 140 | 147.056 | 1.2 | 176.4672 | 1.1 | 194.1139
PUBLIC INSTITUTIONS WATER DEMAND
Profession of people | Number of people | specific water demand | average water demand | seasonal ratio | peak water demand | loss coefficient | designing peak water demand
|  | l/person/day | m3/day | - | m3/day | - | m3/day
worker | 30 | 160 | 4.8 | 1.5 | 7.2 | 1.1 | 7.92
student | 500 | 160 | 80 | 1.5 | 120 | 1.1 | 132
SUM | [6 empty] | 139.92
THE INDUSTRIAL WATER DEMAND
Technological water demand | loss coefficient | designing peak water demand
m3/day | - | m3/day
1000 | 1.1 | 1100
Number of people | specific water demand | average water demand | seasonal ratio | peak water demand | loss coefficient | designing peak water demand
| l/person/day | m3/day | - | m3/day | - | m3/day
100 | 100 | 10 | 1.2 | 12 | 1.1 | 13.2 |  | total consumption will be | 1447.2339

## stress profile
50 | 36 | 31.1817 | 31
100 | 36 | 31.2709 | 31.1817
150 | 36.2 | 31.5164 | 31.2709
200 | 36.5 | 31.9199 | 31.3164